2400 Series

AREA OF REFUGE/RESCUE - Product Specification

- Area of Refuge Command Center, PBX Box, Refuge Call Boxes and Signage

Part 1 - General

- Summary

  - The Area of Refuge Command Center is to be located at a central control point on the first floor or as determined by local Authority having jurisdiction (AHJ). Refuge Call Boxes are to be located on all floors above and below the first floor, ideally next to a stairwell emergency exit or elevator landing on each floor.

  - The Area of Refuge Command Center must be capable of handling a maximum of (12, 16, 28, 36, 56, 76, 92 or 116 please specify) Alpha Refuge Call Boxes. Visual indicators on the Command Center allow Rescue personnel to know which Area of Refuge Refuge Call Box needs assistance. The Command Center must allow Rescue personnel to speak to each Refuge Call Box individually.

  - The Emergency communication hardware shall comply with the Americans with Disabilities Act (ADA). The Refuge Call Box shall have the ability to be programmed with up to 2 emergency phone numbers. Upon activation of the emergency push button, a call will be automatically placed to the Command Center. If no one answers at the Command Center, the Refuge Call Box must dial a secondary location outside the building to activate two way off-site person to person voice communications.

- Submittals

  - Submit Product data sheets. Include operation manuals.

  - Wiring or Shop Diagrams detailing wiring schematics, cabling.

- Construction

  - The Area of Refuge Command Center (RCC2400 series) must have a powder coated steel housing (surface or flush mount), Black coil cord emergency voice Handset and be powered from the PBX Box.

  - PBX Box must be a surface mount enclosure, include connections for 12 up to 116 Refuge Call Boxes and power both the Command Center and the Refuge Call Boxes on a two wire connection. The PBX Box shall be powered from 120vac power with a battery back up that provides power for a minimum of up to 3 hours (Alpha model PWRAPC)

  - The Area of Refuge Refuge Call Boxes (RCB2400 series) must be in full compliance with Americans with Disabilities ACT (ADA).  Refuge Call Boxes require a hands-free speakerphone with an LED to indicate status of call.

  - The Area of Refuge Refuge Call Boxes must allow the programming in of a specific location message of the unit. This allows Rescue personnel to know the location of the activated Refuge Call Box.

  - The Area of Refuge Refuge Call Boxes are to be located no higher than 48” above ground level to ensure conformance with the ADA requirements.

  - The Area of Refuge Refuge Call Boxes must have a Braille faceplate located no higher than 48” for front reach and 54” for side reach above ground level to ensure conformance with the ADA requirements.

  - The Area of Refuge Command Center must provide an audible and visual indicator that a Refuge Call Box has been activated.

  - The Area of Refuge 120vac Power Supply model PWRAPC must be capable of supplying power to a maximum of 36 Call Boxes, one (1) Command Center and one (1) PBX Box. For systems with more than 36 call boxes use the model PWRAPC116 power supply.

- Mounting

  - The Area of Refuge Command Center is to be mounted on a flat wall surface.

  - Areas of Refuge Refuge Call Boxes are to be wall surface or flush mounted.

- Electrical

  - The Refuge Command Center and Refuge Call Boxes are to be powered by the PBX Box.

  - PBX Station shall be powered by the Alpha model PWRAPC power supply when using a maximum of 36 Refuge Call Boxes. For larger systems, the PBX Station shall be powered by the Alpha model PWRAPC116 power supply when using a maximum of 116 Refuge Call Boxes It shall require 120vac power and provide battery back-up capable of providing a minimum of 3 hours of electrical back-up in case of building power failure.

  - The 12 station Command Center shall connect to the PBX Box with a single wire pair. The 56 station Command Center shall connect to the PBX Box via two wire pairs. The 116 station Command Center shall connect to the PBX Box via three wire pairs.

  - Each Refuge Call Box shall connect to the PBX Box with a single wire pair. Wire pairs shall be shielded if near any power runs or other source of electrical interference, otherwise standard pair is acceptable.

  - System shall be in compliance with all state and local Electrical and Building Codes.

- Communications

  - The Refuge Call Boxes shall be an ADA compliant and vandal resistant speakerphone.

  - The Refuge Call Boxes shall be Hands-Free and be a push-button-once to talk system. Once the button has been pushed, the Refuge Call Box will call the Command Center. If no answer at the Command Center, it will automatically call a preprogrammed emergency number.  The Refuge Call Box must be capable of being programmed with up to 2 emergency numbers.

  - Refuge Call Box shall have Location Message capability. Refuge Call Box must have a minimum 25 second recordable message capability, programmable to play 1 or 2 times. Refuge Call Box shall notify called party of the location of the call upon being received at the emergency dispatch center.

  - Refuge Call Box shall be capable of allowing the called party to replay the Location Message if necessary to ensure an understanding of the caller location.

  - If system is not attended to 24 hours a day, the Refuge Call Box must dial a secondary location outside the building to activate two way off-site person to person voice communications.

  - Once call has been made (button pushed), the call can only be terminated by the called party.

  - Refuge Call Box must have a red LED that will light up upon push of the button. The light shall be a solid color when the Refuge Call Box is activated, and will flash when call has been answered.

  - The Refuge Call Box must be capable of being programmed and reprogrammed

on-site.

  - Standard Refuge Call Box features:

    - Two number programming.

    - Operating Temperature of between -40˚F to +150˚F (-40˚ to + 65˚ C)

    - On-Site Programmable.

    - EEPROM memory to protect programming.

- Wiring

  - In order to conform to NFPA code requirements, system shall be installed using Circuit Integrity (CI) 2-hour fire rated low voltage cable (Part# 2PRJS/328 and/or 2PRJS/984), as needed, from the central PBX equipment to the Refuge Call Boxes.

- Signage

  - Adjacent to each (RCB2400 series) Refuge Call Box, shall be installed an instructional sign (Part# RSN7049), with braille lettering.

  - A tactile “Area of Refuge” sign (Part# RSN7044) with raised letters and Braille shall be located at entrance to Area of Refuge.

  - In buildings where lighted EXIT signs are required by code, system shall also include at each Area of Refuge, one 120vac lighted “Area of Refuge” sign (Part# RSN7050) or “Emergency Communications sign (Part# RSN7050E).

- Graphics

  - Area of Refuge Command Center must include wording identifying the location of each Refuge Call Box and light an LED when a particular Refuge Call Box has been activated.

  - Refuge Call Box wording must include “Help Phone”, “International Phone symbol” and raised Braille lettering.

- Product Substitutions

  - No substitutions

- Limited Warranty

The Refuge Command Center and Refuge Call Boxes shall be covered by a two-year limited warranty.

- Manufacturer

The manufacturer shall be:

Alpha Communications®

42 Central Drive

Farmingdale NY 11735-1202

Phone: 631-777-5500

Fax: 631-777-5599

Toll Free: 1-800-666-4800

Website: www.AlphaRefuge.com  or  www.AlphaCommunications.com

Email: info@alphacommunications.com

Part 2 - Execution

## 2.01      INSTALLATION

A.   The entire system shall be installed in a workmanlike manner, in accordance with approved manufacturer’s wiring diagram.  The contractor shall furnish all conduit, wiring, outlet boxes, junction boxes, cabinets and similar devices necessary for the complete installation.  All wiring shall be of the type recommended by the manufacturer, approved by the local Fire Department and specified with in.

B.  All wiring shall be color-coded throughout, to National Electrical Code standards.

## 2.02      FIELD QUALITY CONTROL

A.   The system shall be installed and fully tested.  The system shall be demonstrated to perform all of the functions as specified.

B.   It shall be the responsibility of the installing contractor to assure that construction debris does not adversely affect any sensing devices installed as part of this project.

## 2.03      TESTS / TESTING

- The Area of Refuge system contractor shall pre-test the system in accordance with the 	manufacturer’s requirements and NFPA 72.

B.   As per the NFPA requirements, the complete Area of Refuge system must be inspected on at least 	an annual basis, after the initial installation. The system must be tested for proper power, proper 	functioning of the phone line 	(dial tone and calling), and each Refuge Call Box must be tested.

## 2.04      DOCUMENTATION AND TRAINING

- The contractor shall compile and provide to the owners three (3) complete manuals on the completed system to include operating and maintenance instruction, catalog cuts of all equipment and components, wiring diagrams and a manufacturer’s suggested spare parts list.